## Register
Device | Signal Name | Lib Support | Integration Default | Custom Sensor | Type | Unit | Gain | Address | Quantity | Scope | Comment
INVERTER | MODEL_NAME | Yes |  |  | StringRegister | N/A | 1 | 30000 | 15
INVERTER | SERIAL_NUMBER | Yes |  |  | StringRegister | N/A | 1 | 30015 | 10 | N/A
INVERTER | PN | Yes |  |  | StringRegister | N/A | 1 | 30025 | 10 | N/A
INVERTER | MODEL_ID | Yes |  |  | U16Register | N/A | 1 | 30070 | 1
INVERTER | NB_PV_STRINGS | Yes |  |  | U16Register | N/A | 1 | 30071 | 1 | N/A
INVERTER | NB_MPP_TRACKS | Yes |  |  | U16Register | N/A | 1 | 30072 | 1 | N/A
INVERTER | RATED_POWER | Yes |  | sensor.inverter_rated_power | U32Register | kW | 1000 | 30073 | 2 | N/A
INVERTER | P_MAX | Yes |  | sensor.inverter_maximum_active_power | U32Register | kW | 1000 | 30075 | 2 | N/A
INVERTER | S_MAX | Yes |  | sensor.inverter_maximum_apparent_power | U32Register | kVA | 1000 | 30077 | 2 | N/A
INVERTER | Q_MAX_OUT | Yes |  |  | I32Register | kVar | 1000 | 30079 | 2 | N/A
INVERTER | Q_MAX_IN | Yes |  |  | I32Register | kVar | 1000 | 30081 | 2 | N/A
INVERTER | OFFERING_NAME_OF_SOUTHBOUND_DEVICE_1 | Yes |  |  | StringRegister | N/A | N/A | 30561 | 15
INVERTER | OFFERING_NAME_OF_SOUTHBOUND_DEVICE_2 | Yes |  |  | StringRegister | N/A | N/A | 30576 | 15
INVERTER | OFFERING_NAME_OF_SOUTHBOUND_DEVICE_3 | Yes |  |  | StringRegister | N/A | N/A | 30591 | 15
INVERTER | HARDWARE_VERSION | Yes |  |  | StringRegister | N/A | N/A | 31000 | 15
INVERTER | MONITORING_BOARD_SN | Yes |  |  | StringRegister | N/A | N/A | 31015 | 15
INVERTER | MONITORING_SOFTWARE_VERSION | Yes |  |  | StringRegister | N/A | N/A | 31025 | 15
INVERTER | MASTER_DSP_VERSION | Yes |  |  | StringRegister | N/A | N/A | 31040 | 15
INVERTER | CPLD_VERSION | Yes |  |  | StringRegister | N/A | N/A | 31070 | 15
INVERTER | AFCI_VERSION | Yes |  |  | StringRegister | N/A | N/A | 31085 | 15
INVERTER | DC_MBUS_VERSION | Yes |  |  | StringRegister | N/A | N/A | 31115 | 15
INVERTER | REGKEY | Yes |  |  | StringRegister | N/A | 1 | 31200
INVERTER | STATE_1 | Yes | sensor.inverter_inverter_state |  | U16Register | N/A | 1 | 32000 | 1
INVERTER | STATE_2_#0 | Yes | sensor.inverter_locking_status |  | U16Register | N/A | 1 | 32002 | 1
INVERTER | STATE_2_#1 | Yes | sensor.inverter_pv_connection_status |  | U16Register | N/A | 1 | 32002 | 1
INVERTER | STATE_2_#2 | Yes | sensor.inverter_dsp_data_collection |  | U16Register | N/A | 1 | 32002 | 1
INVERTER | STATE_3_#0 | Yes | sensor.inverter_off_grid_status |  | U32Register | N/A | 1 | 32003 | 1
INVERTER | STATE_3_#1 | Yes | sensor.inverter_off_grid_switch |  | U32Register | N/A | 1 | 32003 | 1
INVERTER | ALARM_1 | Yes | sensor.inverter_alarms |  | U16Register | N/A | 1 | 32008 | 1
INVERTER | ALARM_2 | Yes | sensor.inverter_alarms |  | U16Register | N/A | 1 | 32009 | 1
INVERTER | ALARM_3 | Yes | sensor.inverter_alarms |  | U16Register | N/A | 1 | 32010 | 1
INVERTER | ESN | No | [5 empty] | 32015 |  |  | skip
PV | PV_01_VOLTAGE | Yes | sensor.inverter_pv_1_voltage |  | I16Register | V | 10 | 32016 | 1
PV | PV_01_CURRENT | Yes | sensor.inverter_pv_1_current |  | I16Register | A | 100 | 32017 | 1
PV | PV_02_VOLTAGE | Yes | sensor.inverter_pv_2_voltage |  | I16Register | V | 10 | 32018 | 1
PV | PV_02_CURRENT | Yes | sensor.inverter_pv_2_current |  | I16Register | A | 100 | 32019 | 1
PV | PV_03_VOLTAGE | Yes | sensor.inverter_pv_3_voltage |  | I16Register | V | 10 | 32020 | 1
PV | PV_03_CURRENT | Yes | sensor.inverter_pv_3_current |  | I16Register | A | 100 | 32021 | 1
PV | PV_04_VOLTAGE | Yes | sensor.inverter_pv_4_voltage |  | I16Register | V | 10 | 32022 | 1
PV | PV_04_CURRENT | Yes | sensor.inverter_pv_4_current |  | I16Register | A | 100 | 32023 | 1
PV | PV_05_VOLTAGE | Yes | sensor.inverter_pv_5_voltage |  | I16Register | V | 10 | 32024 | 1
PV | PV_05_CURRENT | Yes | sensor.inverter_pv_5_current |  | I16Register | A | 100 | 32025 | 1
PV | PV_06_VOLTAGE | Yes | sensor.inverter_pv_6_voltage |  | I16Register | V | 10 | 32026 | 1
PV | PV_06_CURRENT | Yes | sensor.inverter_pv_6_current |  | I16Register | A | 100 | 32027 | 1
PV | PV_07_VOLTAGE | Yes | sensor.inverter_pv_7_voltage |  | I16Register | V | 10 | 32028 | 1
PV | PV_07_CURRENT | Yes | sensor.inverter_pv_7_current |  | I16Register | A | 100 | 32029 | 1
PV | PV_08_VOLTAGE | Yes | sensor.inverter_pv_8_voltage |  | I16Register | V | 10 | 32030 | 1
PV | PV_08_CURRENT | Yes | sensor.inverter_pv_8_current |  | I16Register | A | 100 | 32031 | 1
PV | PV_09_VOLTAGE | Yes | sensor.inverter_pv_9_voltage |  | I16Register | V | 10 | 32032 | 1
PV | PV_09_CURRENT | Yes | sensor.inverter_pv_9_current |  | I16Register | A | 100 | 32033 | 1
PV | PV_10_VOLTAGE | Yes | sensor.inverter_pv_10_voltage |  | I16Register | V | 10 | 32034 | 1
PV | PV_10_CURRENT | Yes | sensor.inverter_pv_10_current |  | I16Register | A | 100 | 32035 | 1
PV | PV_11_VOLTAGE | Yes | sensor.inverter_pv_11_voltage |  | I16Register | V | 10 | 32036 | 1
PV | PV_11_CURRENT | Yes | sensor.inverter_pv_11_current |  | I16Register | A | 100 | 32037 | 1
PV | PV_12_VOLTAGE | Yes | sensor.inverter_pv_12_voltage |  | I16Register | V | 10 | 32038 | 1
PV | PV_12_CURRENT | Yes | sensor.inverter_pv_12_current |  | I16Register | A | 100 | 32039 | 1
PV | PV_13_VOLTAGE | Yes | sensor.inverter_pv_13_voltage |  | I16Register | V | 10 | 32040 | 1
PV | PV_13_CURRENT | Yes | sensor.inverter_pv_13_current |  | I16Register | A | 100 | 32041 | 1
PV | PV_14_VOLTAGE | Yes | sensor.inverter_pv_14_voltage |  | I16Register | V | 10 | 32042 | 1
PV | PV_14_CURRENT | Yes | sensor.inverter_pv_14_current |  | I16Register | A | 100 | 32043 | 1
PV | PV_15_VOLTAGE | Yes | sensor.inverter_pv_15_voltage |  | I16Register | V | 10 | 32044 | 1
PV | PV_15_CURRENT | Yes | sensor.inverter_pv_15_current |  | I16Register | A | 100 | 32045 | 1
PV | PV_16_VOLTAGE | Yes | sensor.inverter_pv_16_voltage |  | I16Register | V | 10 | 32046 | 1
PV | PV_16_CURRENT | Yes | sensor.inverter_pv_16_current |  | I16Register | A | 100 | 32047 | 1
PV | PV_17_VOLTAGE | Yes | sensor.inverter_pv_17_voltage |  | I16Register | V | 10 | 32048 | 1
PV | PV_17_CURRENT | Yes | sensor.inverter_pv_17_current |  | I16Register | A | 100 | 32049 | 1
PV | PV_18_VOLTAGE | Yes | sensor.inverter_pv_18_voltage |  | I16Register | V | 10 | 32050 | 1
PV | PV_18_CURRENT | Yes | sensor.inverter_pv_18_current |  | I16Register | A | 100 | 32051 | 1
PV | PV_19_VOLTAGE | Yes | sensor.inverter_pv_19_voltage |  | I16Register | V | 10 | 32052 | 1
PV | PV_19_CURRENT | Yes | sensor.inverter_pv_19_current |  | I16Register | A | 100 | 32053 | 1
PV | PV_20_VOLTAGE | Yes | sensor.inverter_pv_20_voltage |  | I16Register | V | 10 | 32054 | 1
PV | PV_20_CURRENT | Yes | sensor.inverter_pv_20_current |  | I16Register | A | 100 | 32055 | 1
PV | PV_21_VOLTAGE | Yes | sensor.inverter_pv_21_voltage |  | I16Register | V | 10 | 32056 | 1
PV | PV_21_CURRENT | Yes | sensor.inverter_pv_21_current |  | I16Register | A | 100 | 32057 | 1
PV | PV_22_VOLTAGE | Yes | sensor.inverter_pv_22_voltage |  | I16Register | V | 10 | 32058 | 1
PV | PV_22_CURRENT | Yes | sensor.inverter_pv_22_current |  | I16Register | A | 100 | 32059 | 1
PV | PV_23_VOLTAGE | Yes | sensor.inverter_pv_23_voltage |  | I16Register | V | 10 | 32060 | 1
PV | PV_23_CURRENT | Yes | sensor.inverter_pv_23_current |  | I16Register | A | 100 | 32061 | 1
PV | PV_24_VOLTAGE | Yes | sensor.inverter_pv_24_voltage |  | I16Register | V | 10 | 32062 | 1
PV | PV_24_CURRENT | Yes | sensor.inverter_pv_24_current |  | I16Register | A | 100 | 32063 | 1
INVERTER | INPUT_POWER | Yes | sensor.inverter_input_power |  | I32Register | W | 1 | 32064 | 2
INVERTER | GRID_VOLTAGE | Yes |  |  | U16Register | V | 10 | 32066 | 1
INVERTER | LINE_VOLTAGE_A_B | Yes | sensor.inverter_a_b_line_voltage |  | U16Register | V | 10 | 32066 | 1
INVERTER | LINE_VOLTAGE_B_C | Yes | sensor.inverter_b_c_line_voltage |  | U16Register | V | 10 | 32067 | 1
INVERTER | LINE_VOLTAGE_C_A | Yes | sensor.inverter_c_a_line_voltage |  | U16Register | V | 10 | 32068 | 1
INVERTER | PHASE_A_VOLTAGE | Yes | sensor.inverter_phase_a_voltage |  | U16Register | V | 10 | 32069 | 1
INVERTER | PHASE_B_VOLTAGE | Yes | sensor.inverter_phase_b_voltage |  | U16Register | V | 10 | 32070 | 1
INVERTER | PHASE_C_VOLTAGE | Yes | sensor.inverter_phase_c_voltage |  | U16Register | V | 10 | 32071 | 1
INVERTER | GRID_CURRENT | Yes |  |  | I32Register | A | 1000 | 32072 | 2
INVERTER | PHASE_A_CURRENT | Yes | sensor.inverter_phase_a_current |  | I32Register | A | 1000 | 32072 | 2
INVERTER | PHASE_B_CURRENT | Yes | sensor.inverter_phase_b_current |  | I32Register | A | 1000 | 32074 | 2
INVERTER | PHASE_C_CURRENT | Yes | sensor.inverter_phase_c_current |  | I32Register | A | 1000 | 32076 | 2
INVERTER | DAY_ACTIVE_POWER_PEAK | Yes | sensor.inverter_day_active_power_peak |  | I32Register | W | 1 | 32078 | 2
INVERTER | ACTIVE_POWER | Yes | sensor.inverter_active_power |  | I32Register | W | 1 | 32080 | 2
INVERTER | REACTIVE_POWER | Yes | sensor.inverter_reactive_power |  | I32Register | VA | 1 | 32082 | 2
INVERTER | POWER_FACTOR | Yes | sensor.inverter_power_factor |  | I16Register | None | 1000 | 32084 | 1
INVERTER | GRID_FREQUENCY | Yes |  |  | U16Register | Hz | 100 | 32085 | 1
INVERTER | EFFICIENCY | Yes | sensor.inverter_efficiency |  | U16Register | % | 100 | 32086 | 1
INVERTER | INTERNAL_TEMPERATURE | Yes | sensor.inverter_internal_temperature |  | I16Register | °C | 10 | 32087 | 1
INVERTER | INSULATION_RESISTANCE | Yes |  | sensor.inverter_insulation_resistance | U16Register | MOhm | 100 | 32088 | 1
INVERTER | DEVICE_STATUS | Yes | sensor.inverter_device_status |  | U16Register |  | 1 | 32089 | 1
INVERTER | FAULT_CODE | Yes |  |  | U16Register | None | 1 | 32090 | 1
INVERTER | STARTUP_TIME | Yes | sensor.inverter_startup_time |  | TimestampRegister |  |  | 32091 | 2
INVERTER | SHUTDOWN_TIME | Yes | sensor.inverter_shutdown_time |  | TimestampRegister |  |  | 32093 | 2
INVERTER | ACCUMULATED_YIELD_ENERGY | Yes | sensor.inverter_total_yield |  | U32Register | kWh | 100 | 32106 | 2
INVERTER | DAILY_YIELD_ENERGY | Yes | sensor.inverter_daily_yield |  | U32Register | kWh | 100 | 32114 | 2
INVERTER | CAPBANK_RUNNING_TIME | Yes |  |  | U32Register | hour | 10 | 35000 | 2 |  | # SUN2000MA-only register
INVERTER | INTERNAL_FAN_1_RUNNING_TIME | Yes |  |  | U32Register | hour | 10 | 35002 | 2 |  | # SUN2000MA-only register
INVERTER | INV_MODULE_A_TEMP | Yes |  |  | I16Register | °C | 10 | 35021 | 1 |  | # SUN2000MA-only register
INVERTER | INV_MODULE_B_TEMP | Yes |  |  | I16Register | °C | 10 | 35022 | 1 |  | # SUN2000MA-only register
INVERTER | INV_MODULE_C_TEMP | Yes |  |  | I16Register | °C | 10 | 35023 | 1 |  | # SUN2000MA-only register
INVERTER | ANTI_REVERSE_MODULE_1_TEMP | Yes |  |  | I16Register | °C | 10 | 35024 | 1 |  | # SUN2000MA-only register
INVERTER | OUTPUT_BOARD_RELAY_AMBIENT_TEMP_MAX | Yes |  |  | I16Register | °C | 10 | 35025 | 1 |  | # SUN2000MA-only register
INVERTER | ANTI_REVERSE_MODULE_2_TEMP | Yes |  |  | I16Register | °C | 10 | 35027 | 1 |  | # SUN2000MA-only register
INVERTER | DC_TERMINAL_1_2_MAX_TEMP | Yes |  |  | I16Register | °C | 10 | 35028 | 1 |  | # SUN2000MA-only register
INVERTER | AC_TERMINAL_1_2_3_MAX_TEMP | Yes |  |  | I16Register | °C | 10 | 35029 | 1 |  | # SUN2000MA-only register
INVERTER | PHASE_A_DC_COMPONENT_DCI | Yes |  |  | I16Register | A | 1000 | 35038 | 1 |  | # SUN2000MA-only register
INVERTER | PHASE_B_DC_COMPONENT_DCI | Yes |  |  | I16Register | A | 1000 | 35039 | 1 |  | # SUN2000MA-only register
INVERTER | PHASE_C_DC_COMPONENT_DCI | Yes |  |  | I16Register | A | 1000 | 35040 | 1 |  | # SUN2000MA-only register
INVERTER | LEAKAGE_CURRENT_RCD | Yes |  |  | I16Register | mA | 1 | 35041 | 1 |  | # SUN2000MA-only register
INVERTER | POSITIVE_BUS_VOLTAGE | Yes |  |  | I16Register | V | 10 | 35042 | 1 |  | # SUN2000MA-only register
INVERTER | NEGATIVE_BUS_VOLTAGE | Yes |  |  | I16Register | V | 10 | 35043 | 1 |  | # SUN2000MA-only register
INVERTER | BUS_NEGATIVE_VOLTAGE_TO_GROUND | Yes |  |  | I16Register | V | 10 | 35044 | 1 |  | # SUN2000MA-only register
INVERTER | [Management system] Management system status | No | [5 empty] | 35127 |  |  | skip
INVERTER | [Smart I-V Curve Diagnosis] Authorization function | No | [5 empty] | 35136 |  |  | skip
INVERTER | [Smart I-V Curve Diagnosis] License | No | [5 empty] | 35138 |  |  | skip
INVERTER | [Smart I-V Curve Diagnosis] License expiration time | No | [5 empty] | 35139 |  |  | skip
INVERTER | License loading time | No | [5 empty] | 35141 |  |  | skip
INVERTER | License revocation time | No | [5 empty] | 35143 |  |  | skip
INVERTER | License SN | No | [5 empty] | 35145 |  |  | skip
INVERTER | Revocation code | No | [5 empty] | 35155 |  |  | skip
INVERTER | [4G] Module status | No | [5 empty] | 35249 |  |  | skip
INVERTER | [4G] IP address | No | [5 empty] | 35250 |  |  | skip
INVERTER | [4G] Subnet mask | No | [5 empty] | 35252 |  |  | skip
INVERTER | [4G] IMEI | No | [5 empty] | 35254 |  |  | skip
INVERTER | [4G] Signal strength | No | [5 empty] | 35264 |  |  | skip
INVERTER | [4G] Maximum number of PIN attempts | No | [5 empty] | 35265 |  |  | skip
INVERTER | [4G] PIN verification status | No | [5 empty] | 35266 |  |  | skip
INVERTER | Original model name | No | [5 empty] | 35268 |  |  | skip
INVERTER | [Active] Adjustment mode | No | [5 empty] | 35300 |  |  | skip
INVERTER | [Active] Adjustment value | No | [5 empty] | 35302 |  |  | skip
INVERTER | [Active] Adjustment command | No | [5 empty] | 35303 |  |  | skip
INVERTER | [Reactive] Adjustment mode | No | [5 empty] | 35304 |  |  | skip
INVERTER | [Reactive] Adjustment value | No | [5 empty] | 35305 |  |  | skip
INVERTER | [Reactive] Adjustment command | No | [5 empty] | 35307 |  |  | skip
INVERTER | NB_OPTIMIZERS | Yes |  |  | U16Register | None | 1 | 37200 | 1
INVERTER | NB_ONLINE_OPTIMIZERS | Yes | Optimizers online |  | U16Register | None | 1 | 37201 | 1
INVERTER | [Optimizer] Feature data* | No | [5 empty] | 37202 |  |  | skip
INVERTER | SYSTEM_TIME | Yes |  |  | TimestampRegister |  |  | 40000 | 2
INVERTER | [Power grid scheduling] Q-U characteristic curve mode* | No | [5 empty] | 40037 |  |  | skip
INVERTER | [Power grid scheduling] dispatch trigger power (%)* | No | [5 empty] | 40038 |  |  | skip
INVERTER | [Power grid scheduling] Fixed active power derated | No | [5 empty] | 40120 |  |  | skip
INVERTER | [Power grid scheduling] Reactive power compensation (PF) | No | [5 empty] | 40122 |  |  | skip
INVERTER | [Power grid scheduling] Reactive power compensation (Q/S) | No | [5 empty] | 40123 |  |  | skip
INVERTER | [Power grid scheduling] Active power percentage derating (0.1%) | No | [5 empty] | 40125 |  |  | skip
INVERTER | [Power grid scheduling] Fixed active power derated (W) | No | [5 empty] | 40126 |  |  | skip
INVERTER | [Power grid scheduling] Reactive compensation at night (kVar) | No | [5 empty] | 40129 |  |  | skip
INVERTER | [Power grid scheduling] cosφ-P/Pn characteristic curve | No | [5 empty] | 40133 |  |  | skip
INVERTER | [Power grid scheduling] Q-U characteristic curve | No | [5 empty] | 40154 |  |  | skip
INVERTER | [Power grid scheduling] PF-U characteristic curve | No | [5 empty] | 40175 |  |  | skip
INVERTER | [Power grid scheduling] Reactive power adjustment time | No | [5 empty] | 40196 |  |  | skip
INVERTER | [Power grid scheduling] Q-U power percentage to exit scheduling* | No | [5 empty] | 40198 |  |  | skip
INVERTER | STARTUP | Yes |  |  | U16Register | None | 1 | 40200 | 1
INVERTER | SHUTDOWN | Yes |  |  | U16Register | None | 1 | 40201 | 1
INVERTER | GRID_CODE | Yes |  |  | U16Register | rv.GRID_CODES | 1 | 42000 | 1
INVERTER | [Power grid scheduling] Reactive power change gradient | No | [5 empty] | 42015 |  |  | skip
INVERTER | [Power grid scheduling] Active power change gradient | No | [5 empty] | 42017 |  |  | skip
INVERTER | [Power grid scheduling] Schedule instruction valid duration | No | [5 empty] | 42019 |  |  | skip
INVERTER | Failsafe Active Power Limit [kW] [High Accuracy] | No | [5 empty] | 42405 |  |  | skip
INVERTER | TIME_ZONE | Yes |  |  | I16Register | min | 1 | 43006 | 1
INVERTER | [Management system] TLS encryption | No | [5 empty] | 43098 |  |  | skip
INVERTER | WLAN_WAKEUP | Yes |  |  | I16Register |  | 1 | 45052 | 1
INVERTER | Fast power scheduling | No | [5 empty] | 45086 |  |  | skip
INVERTER | Scheduled task | No | [5 empty] | 47674 |  |  | skip
INVERTER | Backup Box model | No | [5 empty] | 48089 |  |  | skip
INVERTER | Phase-toground short-circuit protection | No | [5 empty] | 48090 |  |  | skip
BATTERY | STORAGE_UNIT_1_RUNNING_STATUS | Yes |  |  | U16Register |  | 1 | 37000 | 1
BATTERY | STORAGE_UNIT_1_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 37001 | 2
BATTERY | STORAGE_UNIT_1_BUS_VOLTAGE | Yes |  |  | U16Register | V | 10 | 37003 | 1
BATTERY | STORAGE_UNIT_1_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 37004 | 1
BATTERY | STORAGE_UNIT_1_WORKING_MODE_B | Yes |  |  | U16Register |  | 1 | 37006 | 1
BATTERY | STORAGE_UNIT_1_RATED_CHARGE_POWER | Yes |  | sensor.battery_rated_charge_power | U32Register | W | 1 | 37007 | 2
BATTERY | STORAGE_UNIT_1_RATED_DISCHARGE_POWER | Yes |  | sensor.battery_rated_discharge_power | U32Register | W | 1 | 37009 | 2
BATTERY | STORAGE_UNIT_1_FAULT_ID | Yes |  |  | U16Register | None | 1 | 37014 | 1
BATTERY | STORAGE_UNIT_1_CURRENT_DAY_CHARGE_CAPACITY | Yes |  |  | U32Register | kWh | 100 | 37015 | 2
BATTERY | STORAGE_UNIT_1_CURRENT_DAY_DISCHARGE_CAPACITY | Yes |  |  | U32Register | kWh | 100 | 37017 | 2
BATTERY | STORAGE_UNIT_1_BUS_CURRENT | Yes |  |  | I16Register | A | 10 | 37021 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_TEMPERATURE | Yes |  | sensor.battery_1_temperature | I16Register | °C | 10 | 37022 | 1
BATTERY | STORAGE_UNIT_1_REMAINING_CHARGE_DIS_CHARGE_TIME | Yes |  | sensor.battery_remaining_charge_discharge_time | U16Register | min | 1 | 37025 | 1
BATTERY | STORAGE_UNIT_1_DCDC_VERSION | Yes |  |  | StringRegister |  |  | 37026 | 10
BATTERY | STORAGE_UNIT_1_BMS_VERSION | Yes |  |  | StringRegister |  |  | 37036 | 10
BATTERY | STORAGE_MAXIMUM_CHARGE_POWER | Yes |  |  | U32Register | W | 1 | 37046 | 2
BATTERY | STORAGE_MAXIMUM_DISCHARGE_POWER | Yes |  |  | U32Register | W | 1 | 37048 | 2
BATTERY | STORAGE_UNIT_1_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 37052 | 10
BATTERY | STORAGE_UNIT_1_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 37066 | 2
BATTERY | STORAGE_UNIT_1_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 37068 | 2
BATTERY | STORAGE_UNIT_2_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 37700 | 10
BATTERY | STORAGE_UNIT_2_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 37738 | 1
BATTERY | STORAGE_UNIT_2_RUNNING_STATUS | Yes |  |  | U16Register |  | 1 | 37741 | 1
BATTERY | STORAGE_UNIT_2_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 37743 | 2
BATTERY | STORAGE_UNIT_2_CURRENT_DAY_CHARGE_CAPACITY | Yes |  |  | U32Register | kWh | 100 | 37746 | 2
BATTERY | STORAGE_UNIT_2_CURRENT_DAY_DISCHARGE_CAPACITY | Yes |  |  | U32Register | kWh | 100 | 37748 | 2
BATTERY | STORAGE_UNIT_2_BUS_VOLTAGE | Yes |  |  | U16Register | V | 10 | 37750 | 1
BATTERY | STORAGE_UNIT_2_BUS_CURRENT | Yes |  |  | I16Register | A | 10 | 37751 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 37752 | 1
BATTERY | STORAGE_UNIT_2_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 37753 | 2
BATTERY | STORAGE_UNIT_2_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 37755 | 2
BATTERY | STORAGE_RATED_CAPACITY | Yes |  | sensor.battery_rated_capacity | U32Register | Wh | 1 | 37758 | 2
BATTERY | STORAGE_STATE_OF_CAPACITY | Yes | sensor.battery_state_of_capacity |  | U16Register | % | 10 | 37760 | 1
BATTERY | STORAGE_RUNNING_STATUS | Yes | sensor.battery_status |  | U16Register | rv.StorageStatus | 1 | 37762 | 1
BATTERY | STORAGE_BUS_VOLTAGE | Yes | sensor.battery_bus_voltage |  | U16Register | V | 10 | 37763 | 1
BATTERY | STORAGE_BUS_CURRENT | Yes | sensor.battery_bus_current |  | I16Register | A | 10 | 37764 | 1
BATTERY | STORAGE_CHARGE_DISCHARGE_POWER | Yes | sensor.battery_charge_discharge_power |  | I32Register | W | 1 | 37765 | 2
BATTERY | STORAGE_TOTAL_CHARGE | Yes | sensor.battery_total_charge |  | U32Register | kWh | 100 | 37780 | 2
BATTERY | STORAGE_TOTAL_DISCHARGE | Yes | sensor.battery_total_discharge |  | U32Register | kWh | 100 | 37782 | 2
BATTERY | STORAGE_CURRENT_DAY_CHARGE_CAPACITY | Yes | sensor.battery_day_charge |  | U32Register | kWh | 100 | 37784 | 2
BATTERY | STORAGE_CURRENT_DAY_DISCHARGE_CAPACITY | Yes | sensor.battery_day_discharge |  | U32Register | kWh | 100 | 37786 | 2
BATTERY | STORAGE_UNIT_2_SOFTWARE_VERSION | Yes |  |  | StringRegister |  |  | 37799 | 15
BATTERY | STORAGE_UNIT_1_SOFTWARE_VERSION | Yes |  |  | StringRegister |  |  | 37814 | 15
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37920 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37921 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37922 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37923 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37924 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37925 | 1
BATTERY | STORAGE_SOH_CALIBRATION_STATUS | Yes |  |  | U16Register | None | 1 | 37926 | 1
BATTERY | STORAGE_SOH_CALIBRATION_RELEASE_THE_LOWER_DISCHARGE_LIMIT_OF_THE_SOC | Yes |  |  | U16Register | None | 10 | 37927 | 1
BATTERY | STORAGE_SOH_CALIBRATION_ENABLE_THE_BACKUP_POWER_SOC | Yes |  |  | U16Register | None | 10 | 37928 |  |  | add
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 38200 | 10
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_FIRMWARE_VERSION | Yes |  |  | StringRegister |  |  | 38210 | 15
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_WORKING_STATUS | Yes |  |  | U16Register | None | 1 | 38228 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 38229 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 38233 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_VOLTAGE | Yes |  |  | U16Register | V | 10 | 38235 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_CURRENT | Yes |  |  | I16Register | A | 10 | 38236 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 38238 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 38240 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 38242 | 10
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_FIRMWARE_VERSION | Yes |  |  | StringRegister |  |  | 38252 | 15
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_WORKING_STATUS | Yes |  |  | U16Register | None | 1 | 38270 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 38271 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 38275 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_VOLTAGE | Yes |  |  | U16Register | V | 10 | 38277 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_CURRENT | Yes |  |  | I16Register | A | 10 | 38278 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 38280 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 38282 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 38284 | 10
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_FIRMWARE_VERSION | Yes |  |  | StringRegister |  |  | 38294 | 15
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_WORKING_STATUS | Yes |  |  | U16Register | None | 1 | 38312 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 38313 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 38317 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_VOLTAGE | Yes |  |  | U16Register | V | 10 | 38319 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_CURRENT | Yes |  |  | I16Register | A | 10 | 38320 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 38322 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 38324 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 38326 | 10
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_FIRMWARE_VERSION | Yes |  |  | StringRegister |  |  | 38336 | 15
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_WORKING_STATUS | Yes |  |  | U16Register | None | 1 | 38354 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 38355 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 38359 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_VOLTAGE | Yes |  |  | U16Register | V | 10 | 38361 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_CURRENT | Yes |  |  | I16Register | A | 10 | 38362 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 38364 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 38366 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 38368 | 10
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_FIRMWARE_VERSION | Yes |  |  | StringRegister |  |  | 38378 | 15
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_WORKING_STATUS | Yes |  |  | U16Register | None | 1 | 38396 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 38397 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 38401 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_VOLTAGE | Yes |  |  | U16Register | V | 10 | 38403 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_CURRENT | Yes |  |  | I16Register | A | 10 | 38404 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 38406 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 38408 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_SERIAL_NUMBER | Yes |  |  | StringRegister |  |  | 38410 | 10
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_FIRMWARE_VERSION | Yes |  |  | StringRegister |  |  | 38420 | 15
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_WORKING_STATUS | Yes |  |  | U16Register | None | 1 | 38438 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_STATE_OF_CAPACITY | Yes |  |  | U16Register | % | 10 | 38439 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_CHARGE_DISCHARGE_POWER | Yes |  |  | I32Register | W | 1 | 38443 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_VOLTAGE | Yes |  |  | U16Register | V | 10 | 38445 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_CURRENT | Yes |  |  | I16Register | A | 10 | 38446 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_TOTAL_CHARGE | Yes |  |  | U32Register | kWh | 100 | 38448 | 2
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_TOTAL_DISCHARGE | Yes |  |  | U32Register | kWh | 100 | 38450 | 2
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_MAXIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38452 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_1_MINIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38453 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_MAXIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38454 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_2_MINIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38455 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_MAXIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38456 | 1
BATTERY | STORAGE_UNIT_1_BATTERY_PACK_3_MINIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38457 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_MAXIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38458 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_1_MINIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38459 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_MAXIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38460 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_2_MINIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38461 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_MAXIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38462 | 1
BATTERY | STORAGE_UNIT_2_BATTERY_PACK_3_MINIMUM_TEMPERATURE | Yes |  |  | I16Register | °C | 10 | 38463 | 1
BATTERY | STORAGE_UNIT_1_PRODUCT_MODEL | Yes |  |  | U16Register | rv.StorageProductModel | 1 | 47000 | 1
BATTERY | STORAGE_WORKING_MODE_A | Yes |  |  | I16Register | rv.StorageWorkingModesA | 1 | 47004 | 1
BATTERY | STORAGE_TIME_OF_USE_PRICE | Yes |  |  | I16Register | bool | 1 | 47027 | 1
BATTERY | STORAGE_TIME_OF_USE_PRICE_PERIODS | Yes |  |  | TimeOfUseRegisters |  |  | 47028 | 41
BATTERY | STORAGE_LCOE | Yes |  |  | U32Register | None | 1000 | 47069 | 2
BATTERY | STORAGE_MAXIMUM_CHARGING_POWER | Yes | number.battery_maximum_charging_power |  | U32Register | W | 1 | 47075 | 2
BATTERY | STORAGE_MAXIMUM_DISCHARGING_POWER | Yes | number.battery_maximum_discharging_power |  | U32Register | W | 1 | 47077 | 2
BATTERY | STORAGE_POWER_LIMIT_GRID_TIED_POINT | Yes |  |  | I32Register | W | 1 | 47079 | 2
BATTERY | STORAGE_CHARGING_CUTOFF_CAPACITY | Yes | number.battery_end_of_charge_soc |  | U16Register | % | 10 | 47081 | 1
BATTERY | STORAGE_DISCHARGING_CUTOFF_CAPACITY | Yes | number.battery_end_of_discharge_soc |  | U16Register | % | 10 | 47082 | 1
BATTERY | STORAGE_FORCED_CHARGING_AND_DISCHARGING_PERIOD | Yes |  |  | U16Register | min | 1 | 47083 | 1
BATTERY | STORAGE_FORCED_CHARGING_AND_DISCHARGING_POWER | Yes |  |  | I32Register | min | 1 | 47084 | 2
BATTERY | STORAGE_WORKING_MODE_SETTINGS | Yes | select.battery_working_mode |  | U16Register | rv.StorageWorkingModesC | 1 | 47086 | 1
BATTERY | STORAGE_CHARGE_FROM_GRID_FUNCTION | Yes | switch.battery_charge_from_grid |  | U16Register | bool | 1 | 47087 | 1
BATTERY | STORAGE_GRID_CHARGE_CUTOFF_STATE_OF_CHARGE | Yes | number.battery_grid_charge_cutoff_soc |  | U16Register | % | 10 | 47088 | 1
BATTERY | STORAGE_UNIT_2_PRODUCT_MODEL | Yes |  |  | U16Register | rv.StorageProductModel | 1 | 47089 | 1
BATTERY | STORAGE_FORCIBLE_CHARGE_DISCHARGE_WRITE | Yes |  |  | U16Register | rv.StorageForcibleChargeDischarge | 1 | 47100 | 1
BATTERY | STORAGE_FORCIBLE_CHARGE_DISCHARGE_SOC | Yes |  |  | U16Register | % | 10 | 47101 | 1
BATTERY | STORAGE_BACKUP_POWER_STATE_OF_CHARGE | Yes |  |  | U16Register | % | 10 | 47102 | 1
BATTERY | STORAGE_PRODUCT_MODEL | Yes |  |  | U16Register | rv.StorageProductModel | 1 | 47106 | 1
BATTERY | STORAGE_UNIT_1_NO | Yes |  |  | U16Register | None | 1 | 47107 | 1
BATTERY | STORAGE_UNIT_2_NO | Yes |  |  | U16Register | None | 1 | 47108 | 1
BATTERY | STORAGE_FIXED_CHARGING_AND_DISCHARGING_PERIODS | Yes | sensor.battery_fixed_charging_periods |  | ChargeDischargePeriodRegisters |  |  | 47200 | 41
BATTERY | STORAGE_POWER_OF_CHARGE_FROM_GRID | Yes | number.battery_grid_charge_maximum_power |  | U32Register | W | 1 | 47242 | 2
BATTERY | STORAGE_MAXIMUM_POWER_OF_CHARGE_FROM_GRID | Yes | number.battery_grid_charge_maximum_power |  | U32Register | W | 1 | 47244 | 2
BATTERY | STORAGE_FORCIBLE_CHARGE_DISCHARGE_SETTING_MODE | Yes |  |  | U16Register | None | 1 | 47246 | 1
BATTERY | STORAGE_FORCIBLE_CHARGE_POWER | Yes |  |  | U32Register | None | 1 | 47247 | 2
BATTERY | STORAGE_FORCIBLE_DISCHARGE_POWER | Yes |  |  | U32Register | None | 1 | 47249 | 2
BATTERY | STORAGE_TIME_OF_USE_CHARGING_AND_DISCHARGING_PERIODS | Yes | sensor.battery_time_of_use_periods |  | TimeOfUseRegisters |  |  | 47255 | 43
BATTERY | STORAGE_EXCESS_PV_ENERGY_USE_IN_TOU | Yes | select.battery_excess_pv_energy_use_in_tou |  | U16Register | rv.StorageExcessPvEnergyUseInTOU | 1 | 47299 | 1
BATTERY | ACTIVE_POWER_CONTROL_MODE | Yes |  |  | U16Register | rv.ActivePowerControlMode | 1 | 47415 | 1
BATTERY | MAXIMUM_FEED_GRID_POWER_WATT | Yes |  |  | I32Register | W | 1 | 47416 | 2
BATTERY | MAXIMUM_FEED_GRID_POWER_PERCENT | Yes |  |  | I16Register | % | 10 | 47418 | 1
INVERTER | REMOTE_CHARGE_DISCHARGE_CONTROL_MODE | Yes |  |  | I16Register | rv.RemoteChargeDischargeControlMode | 1 | 47589 | 1
BATTERY | DONGLE_PLANT_MAXIMUM_CHARGE_FROM_GRID_POWER | Yes |  |  | U32Register | W | 1 | 47590 | 2
BATTERY | BACKUP_SWITCH_TO_OFF_GRID | Yes |  |  | U16Register | None | 1 | 47604 | 1
BATTERY | BACKUP_VOLTAGE_INDEPENDEND_OPERATION | Yes |  |  | U16Register | rv.BackupVoltageIndependentOperation | 1 | 47605 | 1
INVERTER | DEFAULT_MAXIMUM_FEED_IN_POWER | Yes |  |  | I32Register | W | 1 | 47675 | 2
INVERTER | DEFAULT_ACTIVE_POWER_CHANGE_GRADIENT | Yes |  |  | U32Register | %/s | 1000 | 47677 | 2
BATTERY | STORAGE_UNIT_1_PACK_1_NO | Yes |  |  | U16Register | None | 1 | 47750 | 1
BATTERY | STORAGE_UNIT_1_PACK_2_NO | Yes |  |  | U16Register | None | 1 | 47751 | 1
BATTERY | STORAGE_UNIT_1_PACK_3_NO | Yes |  |  | U16Register | None | 1 | 47752 | 1
BATTERY | STORAGE_UNIT_2_PACK_1_NO | Yes |  |  | U16Register | None | 1 | 47753 | 1
BATTERY | STORAGE_UNIT_2_PACK_2_NO | Yes |  |  | U16Register | None | 1 | 47754 | 1
BATTERY | STORAGE_UNIT_2_PACK_3_NO | Yes |  |  | U16Register | None | 1 | 47755 | 1
BATTERY | STORAGE_CAPACITY_CONTROL_MODE | Yes | select.battery_capacity_control_mode |  | U16Register | rv.StorageCapacityControlMode | 1 | 47954 | 1
BATTERY | STORAGE_CAPACITY_CONTROL_SOC_PEAK_SHAVING | Yes | number.battery_peak_shaving_soc |  | U16Register | % | 10 | 47955 | 1
BATTERY | STORAGE_CAPACITY_CONTROL_PERIODS | Yes | sensor.battery_capacity_control_periods |  | PeakSettingPeriodRegisters |  |  | 47956 | 64
INVERTER | EMMA | Yes |  |  | U16Register | bool | 1 | 48020 | 1
METER | METER_STATUS | Yes | sensor.power_meter_status |  | U16Register | rv.MeterStatus | 1 | 37100 | 1
METER | GRID_A_VOLTAGE | Yes | sensor.power_meter_phase_a_voltage |  | I32Register | V | 10 | 37101 | 2
METER | GRID_B_VOLTAGE | Yes | sensor.power_meter_phase_b_voltage |  | I32Register | V | 10 | 37103 | 2
METER | GRID_C_VOLTAGE | Yes | sensor.power_meter_phase_c_voltage |  | I32Register | V | 10 | 37105 | 2
METER | ACTIVE_GRID_A_CURRENT | Yes | sensor.power_meter_phase_a_current |  | I32Register | I | 100 | 37107 | 2
METER | ACTIVE_GRID_B_CURRENT | Yes | sensor.power_meter_phase_b_current |  | I32Register | I | 100 | 37109 | 2
METER | ACTIVE_GRID_C_CURRENT | Yes | sensor.power_meter_phase_c_current |  | I32Register | I | 100 | 37111 | 2
METER | POWER_METER_ACTIVE_POWER | Yes | sensor.power_meter_active_power |  | I32Register | W | 1 | 37113 | 2
METER | POWER_METER_REACTIVE_POWER | Yes | sensor.power_meter_reactive_power |  | I32Register | Var | 1 | 37115 | 2
METER | ACTIVE_GRID_POWER_FACTOR | Yes | sensor.power_meter_power_factor |  | I16Register | None | 1000 | 37117 | 1
METER | ACTIVE_GRID_FREQUENCY | Yes | sensor.power_meter_frequency |  | I16Register | Hz | 100 | 37118 | 1
METER | GRID_EXPORTED_ENERGY | Yes | sensor.power_meter_exported |  | I32AbsoluteValueRegister | kWh | 100 | 37119 | 2
METER | GRID_ACCUMULATED_ENERGY | Yes | sensor.power_meter_consumption |  | I32Register | kWh | 100 | 37121 | 2
METER | GRID_ACCUMULATED_REACTIVE_POWER | Yes | sensor.power_meter_reactive_power |  | I32Register | kVarh | 100 | 37123 | 2
METER | METER_TYPE | Yes |  |  | U16Register | rv.MeterType | 1 | 37125 | 1
METER | ACTIVE_GRID_A_B_VOLTAGE | Yes | sensor.power_meter_a_b_line_voltage |  | I32Register | V | 10 | 37126 | 2
METER | ACTIVE_GRID_B_C_VOLTAGE | Yes | sensor.power_meter_b_c_line_voltage |  | I32Register | V | 10 | 37128 | 2
METER | ACTIVE_GRID_C_A_VOLTAGE | Yes | sensor.power_meter_c_a_line_voltage |  | I32Register | V | 10 | 37130 | 2
METER | ACTIVE_GRID_A_POWER | Yes | sensor.power_meter_phase_a_active_power |  | I32Register | W | 1 | 37132 | 2
METER | ACTIVE_GRID_B_POWER | Yes | sensor.power_meter_phase_b_active_power |  | I32Register | W | 1 | 37134 | 2
METER | ACTIVE_GRID_C_POWER | Yes | sensor.power_meter_phase_c_active_power |  | I32Register | W | 1 | 37136 | 2
METER | Meter model detection result | No | [5 empty] | 37138 |  |  | skip
OPTIMIZER | output_power | Yes | Output power
OPTIMIZER | voltage_to_ground | Yes | Voltage to ground
OPTIMIZER | output_voltage | Yes | Output voltage
OPTIMIZER | output_current | Yes | Output current
OPTIMIZER | input_voltage | Yes | Input voltage
OPTIMIZER | input_current | Yes | Input current
OPTIMIZER | temperature | Yes | Temperature
OPTIMIZER | running_status | Yes | Running status
OPTIMIZER | accumulated_energy_yield | Yes | Accumulated energy yield

## Pivot
Row Labels | Count of Lib Support
30000 | 1
MODEL_NAME | 1
30015 | 1
SERIAL_NUMBER | 1
30025 | 1
PN | 1
30070 | 1
MODEL_ID | 1
30071 | 1
NB_PV_STRINGS | 1
30072 | 1
NB_MPP_TRACKS | 1
30073 | 1
RATED_POWER | 1
30075 | 1
P_MAX | 1
30077 | 1
S_MAX | 1
30079 | 1
Q_MAX_OUT | 1
30081 | 1
Q_MAX_IN | 1
30561 | 1
OFFERING_NAME_OF_SOUTHBOUND_DEVICE_1 | 1
30576 | 1
OFFERING_NAME_OF_SOUTHBOUND_DEVICE_2 | 1
30591 | 1
OFFERING_NAME_OF_SOUTHBOUND_DEVICE_3 | 1
31000 | 1
HARDWARE_VERSION | 1
31015 | 1
MONITORING_BOARD_SN | 1
31025 | 1
MONITORING_SOFTWARE_VERSION | 1
31040 | 1
MASTER_DSP_VERSION | 1
31070 | 1
CPLD_VERSION | 1
31085 | 1
AFCI_VERSION | 1
31115 | 1
DC_MBUS_VERSION | 1
31200 | 1
REGKEY | 1
32000 | 1
STATE_1 | 1
32002 | 3
STATE_2_#0 | 1
STATE_2_#1 | 1
STATE_2_#2 | 1
32003 | 2
STATE_3_#0 | 1
STATE_3_#1 | 1
32008 | 1
ALARM_1 | 1
32009 | 1
ALARM_2 | 1
32010 | 1
ALARM_3 | 1
32015 | 1
ESN | 1
32016 | 1
PV_01_VOLTAGE | 1
32017 | 1
PV_01_CURRENT | 1
32018 | 1
PV_02_VOLTAGE | 1
32019 | 1
PV_02_CURRENT | 1
32020 | 1
PV_03_VOLTAGE | 1
32021 | 1
PV_03_CURRENT | 1
32022 | 1
PV_04_VOLTAGE | 1
32023 | 1
PV_04_CURRENT | 1
32024 | 1
PV_05_VOLTAGE | 1
32025 | 1
PV_05_CURRENT | 1
32026 | 1
PV_06_VOLTAGE | 1
32027 | 1
PV_06_CURRENT | 1
32028 | 1
PV_07_VOLTAGE | 1
32029 | 1
PV_07_CURRENT | 1
32030 | 1
PV_08_VOLTAGE | 1
32031 | 1
PV_08_CURRENT | 1
32032 | 1
PV_09_VOLTAGE | 1
32033 | 1
PV_09_CURRENT | 1
32034 | 1
PV_10_VOLTAGE | 1
32035 | 1
PV_10_CURRENT | 1
32036 | 1
PV_11_VOLTAGE | 1
32037 | 1
PV_11_CURRENT | 1
32038 | 1
PV_12_VOLTAGE | 1
32039 | 1
PV_12_CURRENT | 1
32040 | 1
PV_13_VOLTAGE | 1
32041 | 1
PV_13_CURRENT | 1
32042 | 1
PV_14_VOLTAGE | 1
32043 | 1
PV_14_CURRENT | 1
32044 | 1
PV_15_VOLTAGE | 1
32045 | 1
PV_15_CURRENT | 1
32046 | 1
PV_16_VOLTAGE | 1
32047 | 1
PV_16_CURRENT | 1
32048 | 1
PV_17_VOLTAGE | 1
32049 | 1
PV_17_CURRENT | 1
32050 | 1
PV_18_VOLTAGE | 1
32051 | 1
PV_18_CURRENT | 1
32052 | 1
PV_19_VOLTAGE | 1
32053 | 1
PV_19_CURRENT | 1
32054 | 1
PV_20_VOLTAGE | 1
32055 | 1
PV_20_CURRENT | 1
32056 | 1
PV_21_VOLTAGE | 1
32057 | 1
PV_21_CURRENT | 1
32058 | 1
PV_22_VOLTAGE | 1
32059 | 1
PV_22_CURRENT | 1
32060 | 1
PV_23_VOLTAGE | 1
32061 | 1
PV_23_CURRENT | 1
32062 | 1
PV_24_VOLTAGE | 1
32063 | 1
PV_24_CURRENT | 1
32064 | 1
INPUT_POWER | 1
32066 | 2
GRID_VOLTAGE | 1
LINE_VOLTAGE_A_B | 1
32067 | 1
LINE_VOLTAGE_B_C | 1
32068 | 1
LINE_VOLTAGE_C_A | 1
32069 | 1
PHASE_A_VOLTAGE | 1
32070 | 1
PHASE_B_VOLTAGE | 1
32071 | 1
PHASE_C_VOLTAGE | 1
32072 | 2
GRID_CURRENT | 1
PHASE_A_CURRENT | 1
32074 | 1
PHASE_B_CURRENT | 1
32076 | 1
PHASE_C_CURRENT | 1
32078 | 1
DAY_ACTIVE_POWER_PEAK | 1
32080 | 1
ACTIVE_POWER | 1
32082 | 1
REACTIVE_POWER | 1
32084 | 1
POWER_FACTOR | 1
32085 | 1
GRID_FREQUENCY | 1
32086 | 1
EFFICIENCY | 1
32087 | 1
INTERNAL_TEMPERATURE | 1
32088 | 1
INSULATION_RESISTANCE | 1
32089 | 1
DEVICE_STATUS | 1
32090 | 1
FAULT_CODE | 1
32091 | 1
STARTUP_TIME | 1
32093 | 1
SHUTDOWN_TIME | 1
32106 | 1
ACCUMULATED_YIELD_ENERGY | 1
32114 | 1
DAILY_YIELD_ENERGY | 1
35000 | 1
CAPBANK_RUNNING_TIME | 1
35002 | 1
INTERNAL_FAN_1_RUNNING_TIME | 1
35021 | 1
INV_MODULE_A_TEMP | 1
35022 | 1
INV_MODULE_B_TEMP | 1
35023 | 1
INV_MODULE_C_TEMP | 1
35024 | 1
ANTI_REVERSE_MODULE_1_TEMP | 1
35025 | 1
OUTPUT_BOARD_RELAY_AMBIENT_TEMP_MAX | 1
35027 | 1
ANTI_REVERSE_MODULE_2_TEMP | 1
35028 | 1
DC_TERMINAL_1_2_MAX_TEMP | 1
35029 | 1
AC_TERMINAL_1_2_3_MAX_TEMP | 1
35038 | 1
PHASE_A_DC_COMPONENT_DCI | 1
35039 | 1
PHASE_B_DC_COMPONENT_DCI | 1
35040 | 1
PHASE_C_DC_COMPONENT_DCI | 1
35041 | 1
LEAKAGE_CURRENT_RCD | 1
35042 | 1
POSITIVE_BUS_VOLTAGE | 1
35043 | 1
NEGATIVE_BUS_VOLTAGE | 1
35044 | 1
BUS_NEGATIVE_VOLTAGE_TO_GROUND | 1
35127 | 1
[Management system] Management system status | 1
35136 | 1
[Smart I-V Curve Diagnosis] Authorization function | 1
35138 | 1
[Smart I-V Curve Diagnosis] License | 1
35139 | 1
[Smart I-V Curve Diagnosis] License expiration time | 1
35141 | 1
License loading time | 1
35143 | 1
License revocation time | 1
35145 | 1
License SN | 1
35155 | 1
Revocation code | 1
35249 | 1
[4G] Module status | 1
35250 | 1
[4G] IP address | 1
35252 | 1
[4G] Subnet mask | 1
35254 | 1
[4G] IMEI | 1
35264 | 1
[4G] Signal strength | 1
35265 | 1
[4G] Maximum number of PIN attempts | 1
35266 | 1
[4G] PIN verification status | 1
35268 | 1
Original model name | 1
35300 | 1
[Active] Adjustment mode | 1
35302 | 1
[Active] Adjustment value | 1
35303 | 1
[Active] Adjustment command | 1
35304 | 1
[Reactive] Adjustment mode | 1
35305 | 1
[Reactive] Adjustment value | 1
35307 | 1
[Reactive] Adjustment command | 1
37000 | 1
STORAGE_UNIT_1_RUNNING_STATUS | 1
37001 | 1
STORAGE_UNIT_1_CHARGE_DISCHARGE_POWER | 1
37003 | 1
STORAGE_UNIT_1_BUS_VOLTAGE | 1
37004 | 1
STORAGE_UNIT_1_STATE_OF_CAPACITY | 1
37006 | 1
STORAGE_UNIT_1_WORKING_MODE_B | 1
37007 | 1
STORAGE_UNIT_1_RATED_CHARGE_POWER | 1
37009 | 1
STORAGE_UNIT_1_RATED_DISCHARGE_POWER | 1
37014 | 1
STORAGE_UNIT_1_FAULT_ID | 1
37015 | 1
STORAGE_UNIT_1_CURRENT_DAY_CHARGE_CAPACITY | 1
37017 | 1
STORAGE_UNIT_1_CURRENT_DAY_DISCHARGE_CAPACITY | 1
37021 | 1
STORAGE_UNIT_1_BUS_CURRENT | 1
37022 | 1
STORAGE_UNIT_1_BATTERY_TEMPERATURE | 1
37025 | 1
STORAGE_UNIT_1_REMAINING_CHARGE_DIS_CHARGE_TIME | 1
37026 | 1
STORAGE_UNIT_1_DCDC_VERSION | 1
37036 | 1
STORAGE_UNIT_1_BMS_VERSION | 1
37046 | 1
STORAGE_MAXIMUM_CHARGE_POWER | 1
37048 | 1
STORAGE_MAXIMUM_DISCHARGE_POWER | 1
37052 | 1
STORAGE_UNIT_1_SERIAL_NUMBER | 1
37066 | 1
STORAGE_UNIT_1_TOTAL_CHARGE | 1
37068 | 1
STORAGE_UNIT_1_TOTAL_DISCHARGE | 1
37100 | 1
METER_STATUS | 1
37101 | 1
GRID_A_VOLTAGE | 1
37103 | 1
GRID_B_VOLTAGE | 1
37105 | 1
GRID_C_VOLTAGE | 1
37107 | 1
ACTIVE_GRID_A_CURRENT | 1
37109 | 1
ACTIVE_GRID_B_CURRENT | 1
37111 | 1
ACTIVE_GRID_C_CURRENT | 1
37113 | 1
POWER_METER_ACTIVE_POWER | 1
37115 | 1
POWER_METER_REACTIVE_POWER | 1
37117 | 1
ACTIVE_GRID_POWER_FACTOR | 1
37118 | 1
ACTIVE_GRID_FREQUENCY | 1
37119 | 1
GRID_EXPORTED_ENERGY | 1
37121 | 1
GRID_ACCUMULATED_ENERGY | 1
37123 | 1
GRID_ACCUMULATED_REACTIVE_POWER | 1
37125 | 1
METER_TYPE | 1
37126 | 1
ACTIVE_GRID_A_B_VOLTAGE | 1
37128 | 1
ACTIVE_GRID_B_C_VOLTAGE | 1
37130 | 1
ACTIVE_GRID_C_A_VOLTAGE | 1
37132 | 1
ACTIVE_GRID_A_POWER | 1
37134 | 1
ACTIVE_GRID_B_POWER | 1
37136 | 1
ACTIVE_GRID_C_POWER | 1
37138 | 1
Meter model detection result | 1
37200 | 1
NB_OPTIMIZERS | 1
37201 | 1
NB_ONLINE_OPTIMIZERS | 1
37202 | 1
[Optimizer] Feature data* | 1
37700 | 1
STORAGE_UNIT_2_SERIAL_NUMBER | 1
37738 | 1
STORAGE_UNIT_2_STATE_OF_CAPACITY | 1
37741 | 1
STORAGE_UNIT_2_RUNNING_STATUS | 1
37743 | 1
STORAGE_UNIT_2_CHARGE_DISCHARGE_POWER | 1
37746 | 1
STORAGE_UNIT_2_CURRENT_DAY_CHARGE_CAPACITY | 1
37748 | 1
STORAGE_UNIT_2_CURRENT_DAY_DISCHARGE_CAPACITY | 1
37750 | 1
STORAGE_UNIT_2_BUS_VOLTAGE | 1
37751 | 1
STORAGE_UNIT_2_BUS_CURRENT | 1
37752 | 1
STORAGE_UNIT_2_BATTERY_TEMPERATURE | 1
37753 | 1
STORAGE_UNIT_2_TOTAL_CHARGE | 1
37755 | 1
STORAGE_UNIT_2_TOTAL_DISCHARGE | 1
37758 | 1
STORAGE_RATED_CAPACITY | 1
37760 | 1
STORAGE_STATE_OF_CAPACITY | 1
37762 | 1
STORAGE_RUNNING_STATUS | 1
37763 | 1
STORAGE_BUS_VOLTAGE | 1
37764 | 1
STORAGE_BUS_CURRENT | 1
37765 | 1
STORAGE_CHARGE_DISCHARGE_POWER | 1
37780 | 1
STORAGE_TOTAL_CHARGE | 1
37782 | 1
STORAGE_TOTAL_DISCHARGE | 1
37784 | 1
STORAGE_CURRENT_DAY_CHARGE_CAPACITY | 1
37786 | 1
STORAGE_CURRENT_DAY_DISCHARGE_CAPACITY | 1
37799 | 1
STORAGE_UNIT_2_SOFTWARE_VERSION | 1
37814 | 1
STORAGE_UNIT_1_SOFTWARE_VERSION | 1
37920 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_SOH_CALIBRATION_STATUS | 1
37921 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_SOH_CALIBRATION_STATUS | 1
37922 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_SOH_CALIBRATION_STATUS | 1
37923 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_SOH_CALIBRATION_STATUS | 1
37924 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_SOH_CALIBRATION_STATUS | 1
37925 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_SOH_CALIBRATION_STATUS | 1
37926 | 1
STORAGE_SOH_CALIBRATION_STATUS | 1
37927 | 1
STORAGE_SOH_CALIBRATION_RELEASE_THE_LOWER_DISCHARGE_LIMIT_OF_THE_SOC | 1
37928 | 1
STORAGE_SOH_CALIBRATION_ENABLE_THE_BACKUP_POWER_SOC | 1
38200 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_SERIAL_NUMBER | 1
38210 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_FIRMWARE_VERSION | 1
38228 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_WORKING_STATUS | 1
38229 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_STATE_OF_CAPACITY | 1
38233 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_CHARGE_DISCHARGE_POWER | 1
38235 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_VOLTAGE | 1
38236 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_CURRENT | 1
38238 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_TOTAL_CHARGE | 1
38240 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_TOTAL_DISCHARGE | 1
38242 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_SERIAL_NUMBER | 1
38252 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_FIRMWARE_VERSION | 1
38270 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_WORKING_STATUS | 1
38271 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_STATE_OF_CAPACITY | 1
38275 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_CHARGE_DISCHARGE_POWER | 1
38277 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_VOLTAGE | 1
38278 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_CURRENT | 1
38280 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_TOTAL_CHARGE | 1
38282 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_TOTAL_DISCHARGE | 1
38284 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_SERIAL_NUMBER | 1
38294 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_FIRMWARE_VERSION | 1
38312 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_WORKING_STATUS | 1
38313 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_STATE_OF_CAPACITY | 1
38317 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_CHARGE_DISCHARGE_POWER | 1
38319 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_VOLTAGE | 1
38320 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_CURRENT | 1
38322 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_TOTAL_CHARGE | 1
38324 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_TOTAL_DISCHARGE | 1
38326 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_SERIAL_NUMBER | 1
38336 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_FIRMWARE_VERSION | 1
38354 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_WORKING_STATUS | 1
38355 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_STATE_OF_CAPACITY | 1
38359 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_CHARGE_DISCHARGE_POWER | 1
38361 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_VOLTAGE | 1
38362 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_CURRENT | 1
38364 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_TOTAL_CHARGE | 1
38366 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_TOTAL_DISCHARGE | 1
38368 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_SERIAL_NUMBER | 1
38378 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_FIRMWARE_VERSION | 1
38396 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_WORKING_STATUS | 1
38397 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_STATE_OF_CAPACITY | 1
38401 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_CHARGE_DISCHARGE_POWER | 1
38403 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_VOLTAGE | 1
38404 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_CURRENT | 1
38406 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_TOTAL_CHARGE | 1
38408 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_TOTAL_DISCHARGE | 1
38410 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_SERIAL_NUMBER | 1
38420 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_FIRMWARE_VERSION | 1
38438 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_WORKING_STATUS | 1
38439 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_STATE_OF_CAPACITY | 1
38443 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_CHARGE_DISCHARGE_POWER | 1
38445 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_VOLTAGE | 1
38446 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_CURRENT | 1
38448 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_TOTAL_CHARGE | 1
38450 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_TOTAL_DISCHARGE | 1
38452 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_MAXIMUM_TEMPERATURE | 1
38453 | 1
STORAGE_UNIT_1_BATTERY_PACK_1_MINIMUM_TEMPERATURE | 1
38454 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_MAXIMUM_TEMPERATURE | 1
38455 | 1
STORAGE_UNIT_1_BATTERY_PACK_2_MINIMUM_TEMPERATURE | 1
38456 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_MAXIMUM_TEMPERATURE | 1
38457 | 1
STORAGE_UNIT_1_BATTERY_PACK_3_MINIMUM_TEMPERATURE | 1
38458 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_MAXIMUM_TEMPERATURE | 1
38459 | 1
STORAGE_UNIT_2_BATTERY_PACK_1_MINIMUM_TEMPERATURE | 1
38460 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_MAXIMUM_TEMPERATURE | 1
38461 | 1
STORAGE_UNIT_2_BATTERY_PACK_2_MINIMUM_TEMPERATURE | 1
38462 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_MAXIMUM_TEMPERATURE | 1
38463 | 1
STORAGE_UNIT_2_BATTERY_PACK_3_MINIMUM_TEMPERATURE | 1
40000 | 1
SYSTEM_TIME | 1
40037 | 1
[Power grid scheduling] Q-U characteristic curve mode* | 1
40038 | 1
[Power grid scheduling] dispatch trigger power (%)* | 1
40120 | 1
[Power grid scheduling] Fixed active power derated | 1
40122 | 1
[Power grid scheduling] Reactive power compensation (PF) | 1
40123 | 1
[Power grid scheduling] Reactive power compensation (Q/S) | 1
40125 | 1
[Power grid scheduling] Active power percentage derating (0.1%) | 1
40126 | 1
[Power grid scheduling] Fixed active power derated (W) | 1
40129 | 1
[Power grid scheduling] Reactive compensation at night (kVar) | 1
40133 | 1
[Power grid scheduling] cosφ-P/Pn characteristic curve | 1
40154 | 1
[Power grid scheduling] Q-U characteristic curve | 1
40175 | 1
[Power grid scheduling] PF-U characteristic curve | 1
40196 | 1
[Power grid scheduling] Reactive power adjustment time | 1
40198 | 1
[Power grid scheduling] Q-U power percentage to exit scheduling* | 1
40200 | 1
STARTUP | 1
40201 | 1
SHUTDOWN | 1
42000 | 1
GRID_CODE | 1
42015 | 1
[Power grid scheduling] Reactive power change gradient | 1
42017 | 1
[Power grid scheduling] Active power change gradient | 1
42019 | 1
[Power grid scheduling] Schedule instruction valid duration | 1
42405 | 1
Failsafe Active Power Limit [kW] [High Accuracy] | 1
43006 | 1
TIME_ZONE | 1
43098 | 1
[Management system] TLS encryption | 1
45052 | 1
WLAN_WAKEUP | 1
45086 | 1
Fast power scheduling | 1
47000 | 1
STORAGE_UNIT_1_PRODUCT_MODEL | 1
47004 | 1
STORAGE_WORKING_MODE_A | 1
47027 | 1
STORAGE_TIME_OF_USE_PRICE | 1
47028 | 1
STORAGE_TIME_OF_USE_PRICE_PERIODS | 1
47069 | 1
STORAGE_LCOE | 1
47075 | 1
STORAGE_MAXIMUM_CHARGING_POWER | 1
47077 | 1
STORAGE_MAXIMUM_DISCHARGING_POWER | 1
47079 | 1
STORAGE_POWER_LIMIT_GRID_TIED_POINT | 1
47081 | 1
STORAGE_CHARGING_CUTOFF_CAPACITY | 1
47082 | 1
STORAGE_DISCHARGING_CUTOFF_CAPACITY | 1
47083 | 1
STORAGE_FORCED_CHARGING_AND_DISCHARGING_PERIOD | 1
47084 | 1
STORAGE_FORCED_CHARGING_AND_DISCHARGING_POWER | 1
47086 | 1
STORAGE_WORKING_MODE_SETTINGS | 1
47087 | 1
STORAGE_CHARGE_FROM_GRID_FUNCTION | 1
47088 | 1
STORAGE_GRID_CHARGE_CUTOFF_STATE_OF_CHARGE | 1
47089 | 1
STORAGE_UNIT_2_PRODUCT_MODEL | 1
47100 | 1
STORAGE_FORCIBLE_CHARGE_DISCHARGE_WRITE | 1
47101 | 1
STORAGE_FORCIBLE_CHARGE_DISCHARGE_SOC | 1
47102 | 1
STORAGE_BACKUP_POWER_STATE_OF_CHARGE | 1
47106 | 1
STORAGE_PRODUCT_MODEL | 1
47107 | 1
STORAGE_UNIT_1_NO | 1
47108 | 1
STORAGE_UNIT_2_NO | 1
47200 | 1
STORAGE_FIXED_CHARGING_AND_DISCHARGING_PERIODS | 1
47242 | 1
STORAGE_POWER_OF_CHARGE_FROM_GRID | 1
47244 | 1
STORAGE_MAXIMUM_POWER_OF_CHARGE_FROM_GRID | 1
47246 | 1
STORAGE_FORCIBLE_CHARGE_DISCHARGE_SETTING_MODE | 1
47247 | 1
STORAGE_FORCIBLE_CHARGE_POWER | 1
47249 | 1
STORAGE_FORCIBLE_DISCHARGE_POWER | 1
47255 | 1
STORAGE_TIME_OF_USE_CHARGING_AND_DISCHARGING_PERIODS | 1
47299 | 1
STORAGE_EXCESS_PV_ENERGY_USE_IN_TOU | 1
47415 | 1
ACTIVE_POWER_CONTROL_MODE | 1
47416 | 1
MAXIMUM_FEED_GRID_POWER_WATT | 1
47418 | 1
MAXIMUM_FEED_GRID_POWER_PERCENT | 1
47589 | 1
REMOTE_CHARGE_DISCHARGE_CONTROL_MODE | 1
47590 | 1
DONGLE_PLANT_MAXIMUM_CHARGE_FROM_GRID_POWER | 1
47604 | 1
BACKUP_SWITCH_TO_OFF_GRID | 1
47605 | 1
BACKUP_VOLTAGE_INDEPENDEND_OPERATION | 1
47674 | 1
Scheduled task | 1
47675 | 1
DEFAULT_MAXIMUM_FEED_IN_POWER | 1
47677 | 1
DEFAULT_ACTIVE_POWER_CHANGE_GRADIENT | 1
47750 | 1
STORAGE_UNIT_1_PACK_1_NO | 1
47751 | 1
STORAGE_UNIT_1_PACK_2_NO | 1
47752 | 1
STORAGE_UNIT_1_PACK_3_NO | 1
47753 | 1
STORAGE_UNIT_2_PACK_1_NO | 1
47754 | 1
STORAGE_UNIT_2_PACK_2_NO | 1
47755 | 1
STORAGE_UNIT_2_PACK_3_NO | 1
47954 | 1
STORAGE_CAPACITY_CONTROL_MODE | 1
47955 | 1
STORAGE_CAPACITY_CONTROL_SOC_PEAK_SHAVING | 1
47956 | 1
STORAGE_CAPACITY_CONTROL_PERIODS | 1
48020 | 1
EMMA | 1
48089 | 1
Backup Box model | 1
48090 | 1
Phase-toground short-circuit protection | 1
(blank)
accumulated_energy_yield
input_current
input_voltage
output_current
output_power
output_voltage
running_status
temperature
voltage_to_ground
(blank)
Grand Total | 365